## Data Sheet
|  |  | Design Data | [9 empty] | Measured Data
Sr. | AHU/Air Washer/ FDV/ Equipment Identification | Location | Year of Installation | Design Flow, CFM | Design Static Pressure (pascal) | No. of Fan in AHU | Total Installed Motor KW | Installed Motor RPM | Motor Efficieny Value, % | Motor Efficiency Class, IE1/IE2/IE3 | Belt Drive or Direct Mount Motor | VFD Provided (Yes/No) | VFD Operating Frequency | Measured Flow CFM | Measured Static mmWC | Measured Motor input KW | Operating Hours/Day | Operating Days/Annum | Unit Rate BDT/KWH
1 | AHU 4 | PP GOAT mixer area & Sankalp packaging |  | 26000 | 1314 | 1 | 30 | 1400 | 93% | IE2 | Belt Drive | Yes | N/A | Consider Design Data |  | 27 | 24 | 348 | 8.5
2 | AHU 5 | PP LP Packaging |  | 14910 | 1296 | 1 | 15 | 1400 | 93% | IE2 | Belt Drive | Yes | N/A |  |  | 13.5 | 24 | 348 | 8.5
3 | AHU 6 | PP LP Process |  | 24120 | 1295 | 1 | 22 | 1400 | 93% | IE2 | Belt Drive | Yes | N/A |  |  | 19.8 | 24 | 348 | 8.5
4 | AHU 7 | PP LP Process |  | 28550 | 1294 | 1 | 30 | 1400 | 93% | IE2 | Belt Drive | Yes | N/A |  |  | 27 | 24 | 348 | 8.5
Check requirement sheet for required technical specification, scope of supply and installation

## Requirement
S. No | Item Description | Specifications | Quantity | Article No | Unit Price | Total Cost
1 | Technical Specification | Technical Specifications 1. Fan Type: High-efficiency backward curve aerofoil design EC Fan / Axial Fan 2. Impeller Material: ZAmid / Aluminium GRP 3. Motor Efficiency Class: IE5 (inbuild vfd) 4. Operating Voltage: 400V, 3 Phase, 50Hz 5. Control Type: Integrated speed control via 0–10V or Modbus / VFD control 6. VFD: Danfoss or equivalent 7. Electrical Panel: Rittal or equivalent 8. IP Rating: Minimum IP55 (Fan Enclosure) 9. Electrical Connector Safety Rating: IP65 10. Wiring: Plug-and-play connectors for ease of installation 11. Control Automation: Provision for automatic fan speed control based on temperature or pressure feedback 12. BMS Integration: Fully compatible with existing or proposed Building Management System (BMS); supports display and monitoring of real-time operating parameters 13. Delivery Timeline: 8–10 weeks from the date of order confirmation 14. Energy Savings Guarantee: Minimum 40% energy savings, validated with before-and-after retrofit measurement data 15. Local Support: Availability of local service and support in Bangladesh 16. Warranty: Comprehensive 2-year warranty on supplied components
2 | Scope of Supply | Scope of Supply 1. Fan motor set (EC Fan / Axial Fan with IE5 motor) 2. Pressure or temperature sensor and controller / VFD panel 3. Structural support/modifications required for integration with existing air washer units 4. Power and communication cables 5. Installation accessories: Saddle clips, cable ties, thimbles, etc. 6. TriBox, cable glands, and connectors 7. Cable trays. 8. Dismantling of existing fan and motor assembly 9. Shifting dismantled components to the designated scrap yard
3 | Scope of installation | Scope of Installation 1. Measurement of baseline parameters: o Airflow (CFM) o Static pressure (Pascal) o Motor power consumption (kW) 2. Supervision for Installation of new high-efficiency fan motor set 3. Supervision for Installation of sensors, controllers, or VFD panel as applicable 4. Supervision for Complete installation of power and control wiring, including cable trays within air washer units 5. Commissioning of newly installed fans 6. Verification of airflow and static pressure to match or exceed baseline performance 7. Establishment and documentation of minimum 35% energy savings post-retrofit, maintaining equivalent or improved delivery
4 | AHU-4 | Flow -26000 , Static - 1300 pascal |  |  |  | 0
5 | AHU-5 | Flow -15000 , Static - 1300 pascal |  |  |  | 0
6 | AHU-6 | Flow -24000 , Static - 1200 pascal |  |  |  | 0
7 | AHU-7 | Flow -28000 , Static - 1200 pascal |  |  |  | 0
10 | Closeloop Controller / VFD Panel | - |  |  |  | 0
11 | Installation & Commissioning | - |  |  |  | 0
12 | P&F | - |  |  |  | 0
13 | Freight | - |  |  |  | 0
Total | [5 empty] | 0